SECTION 233600 – AIR TERMINAL UNITS

- GENERAL

      - SUMMARY

        - Related Documents:

          - Drawings and general provisions of the Subcontract apply to this Section.

          - Review these documents for coordination with additional requirements and information that apply to work under this Section.

        - Section Includes:

          - Fan powered terminal units.

          - Constant volume terminal units.

          - Variable volume terminal units.

          - Dual duct terminal units.

          - Variable volume regulators.

          - Integral sound attenuator.

          - Integral heating coils.

          - Integral damper motor operators.

          - Integral controls.

        - Related Sections:

          - Division 01 Section "General Requirements."

          - Division 01 Section "Special Procedures."

          - Division 23 Section "Common Motor Requirements for HVAC Equipment".

          - Division 23 Section "Hydronic Piping" for connections to heating coils.

          - Division 23 Section "Hydronic Specialties" for connections to heating coils.

          - Division 23 Section "Metal Ducts".

          - Division 23 Section "Metal Ducts Fittings" for backdraft dampers.

          - Division 23 Section "Air Outlets and Inlets".

          - Division 23 Section "Instrumentation and Control Devices for HVAC" for thermostats and control components.

        - Products Furnished But Not Installed Under This Section:

          - Thermostats

      - REFERENCES

        - General:

          - The following documents form part of the Specifications to the extent stated. Where differences exist between codes and standards, the one affording the greatest protection shall apply.

          - Unless otherwise noted, the referenced standard edition is the current one at the time of commencement of the Work.

          - Refer to Division 01 Section "General Requirements" for the list of applicable regulatory requirements.

          - Refer to Division 23 Section "Common Results for HVAC" for codes and standards, and other general requirements.

        - NFPA 90A - Installation of Air Conditioning and Ventilation Systems.

        - UL 181 - Factory-Made Air Ducts and Connectors.

        - ADC 1062 - Air Distribution and Control Device Test Code.

        - AHRI 880 – Performance Rating of Air Terminals

        - UL 181, meets the Erosion Testing requirements

        - ASTM B-117 – 125 Hour Salt Spray Test

        - ASHRAE 130 Laboratory Methods of Testing Air Terminal Units

      - SUBMITTALS

        - Submit under provisions of Division 23 Section "Common Results for HVAC, Review of Materials and Division 01 Section "General Requirements."

        - Submit shop drawings indicating configuration, general assembly, and materials used in fabrication.

        - Submit product data indicating configuration, general assembly, and materials used in fabrication.  Include catalog performance ratings which indicate air flow, static pressure, and NC designation.

        - Include schedules listing discharge and radiated sound power level for each of second through sixth octave bands at inlet static pressures of one to three inch wg (250 to 1000 Pa).

        - Submit manufacturer’s installation instructions.

        - Operation and Maintenance Data:

          - Include manufacturer’s descriptive literature, operating instructions, maintenance and repair data, and parts lists.

      - QUALITY ASSURANCE

        - Manufacturer's Qualifications: Company specializing in manufacturing the products specified in this Section with minimum 10 years documented experience.

        - ASHRAE Compliance:  Applicable requirements in ASHRAE 62.1-2004, Section 5 - "Systems and Equipment" and Section 7 - "Construction and Startup."

        - AHRI 880 – Performance Testing for Air Terminal Units

        - Mockup:  Provide mockup of typical [exterior] building module.

          - If acceptable, mockup will demonstrate minimum standard for the Work.  Mockup may [not] remain as part of the Work.

      - WARRANTY

        - Provide 12 month after installation or 18 months after shipment, whichever comes first, part(s) only warranty.

- PRODUCTS

      - MANUFACTURERS

        - Johnson Controls

        - Approved Equal

      - MANUFACTURED UNITS

        - Ceiling mounted [constant] [variable air volume] [fan powered] supply air control terminals for connection to [single] [dual] [low] [medium] [high] pressure duct, central air systems, with [mechanical] [pneumatic] [system powered] [no] constant volume control, [pneumatic,] [electric,] [system powered,] [variable volume controls,] [electric.] [Hot water.] [Heating coils.]

        - Identify each airflow unit with clearly marked identification label and airflow indicator.  Label shall include unit nominal air flow, maximum factory set air flow, minimum factory set air flow, and heat / coil type.

      - FABRICATION

        - Casings: Terminals shall be constructed of not less than 22 gauge galvanized steel, able to withstand a 125 hour salt spray test per ASTM B-117. The terminal casing shall be mechanically assembled (spot welded casings are not acceptable). Casing shall have bottom access to gain access to the fan assembly. The opening shall be sufficiently large to allow complete removal of the fan if necessary

        - Lining: Internally lined with 3/4" thick fiberglass insulation, rated for a maximum air velocity of 5000 f.p.m. .  In addition to using adhesive complying with NFPA 90A, the insulation shall incorporate a secondary mechanical fastener attached to the unit casing wall (clench nail).  Adhesive as the only method of fastening the insulation to the casing is not acceptable.  Maximum thermal conductivity shall be 0.24 (BTU • in) / (hr. • ft2 • °F). Insulation must meet all requirements of ASTM C1071 (including C665), UL 181 for erosion, and carry a 25/50 rating for flame spread/ smoke developed per ASTM E-84, UL 723 and NFPA 90A. Raw insulation edges on the discharge of the unit must be covered with metal liner to eliminate flaking of insulation during field duct connections. Simple “buttering” of raw edges with an approved sealant is not acceptable.

        - Alternate Liners:

          - FOIL FACED INSULATION; Insulation shall be covered with scrim backed foil facing. All insulation edges shall be covered with foil or metal nosing.  Insulation shall meet ASTM C1136 for low permeance vapor retarders and ASTM C665 for biological growth in mineral-fiber blanket thermal insulation.

          - DOUBLE WALL CONSTRUCTION; The terminal casing shall be double wall construction using a 22 gauge galvanized metal liner with a chromate finish covering all insulation.

          - LOW TEMPERATURE CONSTRUCTION: Terminals shall be designed for use with primary airflow temperatures as low as 46°F and maximum ceiling plenum conditions of 78°F and 60% R.H.  In addition to other design criteria, the primary air valve shall be thermally isolated from the terminal casing.  The damper shaft shall be made from non-conducting thermoplastic composite material.  Metal shafts will not be acceptable.

        - Airstream Surfaces:  Surfaces in contact with the airstream shall comply with requirements in ASHRAE 62.1-2004.

        - Assembly: Air volume damper, fans, and controls in single cabinet  shall not extend past the top or bottom of unit casing

        - Plenum Air Inlets: [Flange or S and drive connections] for duct attachment.

        - Plenum Air Outlets: S and drive connections [.] [And blower discharge with one inch (25 mm) flange duct attachment.]

        - Mixing Sections (Dual Duct): Multiple deflection baffles designed for mixing air with minimum pressure loss.

      - pRIMARY aIR valve

        - Locate air volume damper [and automatic flow control] assembly inside unit casing.  The primary air valve shall consist of a minimum 22 gauge cylindrical body that includes embossment rings for rigidity. The damper blade shall be connected to a solid shaft by means of an integral molded sleeve which does not require screw or bolt fasteners. Key damper blades into shaft with nylon fitted pivot points.

        - The shaft shall be manufactured of a low thermal conducting composite material, and include a molded damper position indicator visible from the exterior of the unit Air volume control damper shall be factory calibrated assembly consisting of damper and damper shaft extension for connection to externally mounted control actuator.

        - The damper shall pivot in self-lubricating bearings, and shall be mounted on the exterior of the terminal for ease of service

        - The valve assembly shall include internal mechanical stops for both full open and closed positions.

        - The damper blade seal shall be secured without use of adhesives.

        - The air valve leakage shall not exceed 1% of maximum inlet rated airflow at 3" W.G. inlet pressure.

      - Primary airflow Sensor

        - For inlet diameters 6" or greater, the differential pressure airflow sensor shall traverse the duct along two perpendicular diameters. Cylindrically shaped inlets shall utilize the equal cross sectional area or log-linear traverse method. Single axis sensor shall not be acceptable for duct diameters 6" or larger.

        - A minimum of 12 total pressure sensing points shall be utilized. The total pressure inputs shall be averaged using a pressure chamber located at the center of the sensor. A sensor that delivers the differential pressure signal from one end of the sensor is not acceptable.

        - The sensor shall output an amplified differential pressure signal that is at least 2.3 times the equivalent velocity pressure signal obtained from a conventional pitot tube. The sensor shall develop a differential pressure of 0.015" w.g. at an air velocity of ≤ 325 FPM. Documentation shall be submitted which substantiates this requirement. Balancing taps and airflow calibration charts shall be provided for field airflow measurements.

      - HEATING COILS

        - Hot Water Heating Coil: 1/2 inch or 3/8 inch copper tube mechanically expanded into aluminum plate fins, leak tested under water shall be hydrostatically tested at a minimum of 450 PSIG under water, and rated for a maximum 300 PSIG working pressure at 200°F.

          - Shall have 22 gauge galvanized sheet metal casing Coil to be constructed of pure aluminum fins with full fin collars to assure accurate fin spacing and maximum tube contact.

          - Fins shall be spaced with a minimum of 10 per inch and mechanically fixed to seamless copper tubes for maximum heat transfer.

        - Electric Heating Coil: Terminal shall include an integral electric heater where indicated on the plans. The heater cabinet shall be constructed of not less than 20 gauge galvanized steel stainless steel cabinets. Heater shall have a hinged access panel for entry to the controls.

          - A power disconnect shall be furnished to render the heater non-operational. Heater shall be furnished with all controls necessary for safe operation and full compliance with UL 1995 and National Electric Code requirements.

          - Heater shall have a single point electrical connection. It shall include a primary disc-type automatic reset high temperature limit, secondary high limit(s), Ni-Chrome elements, and fusing per UL and NEC.

          - Heater shall have complete wiring diagram with label indicating power requirement and kW output.

          - Heater shall be interlocked with fan terminal so as to preclude operation of the heater when the fan is not running.

      - FILTERS:

        - Standard Option. Terminals shall include a 1" thick disposable fiberglass filter.  Filter shall be secured with quick release clips, allowing removal without horizontal sliding.

        - Extra Filters:  Provide two total filters per fan terminal unit to allow for secondary filter change out 2 weeks prior to occupancy.

      - FAN ASSEMBLY

Forward curved centrifugal type fan with direct drive permanent split capacitor type, with optional electronic commutated motor (ECM), thermally protected motor. ECM MOTOR; Fan motor shall be electronically commutated motor.  The motor shall be brushless DC controlled by an integrated controller / inverter that operates the wound stator and senses rotor position to electrically commutate the stator. Motor shall be permanent magnet type with near-zero rotor losses designed for synchronous rotation. The EC motor shall maintain minimum 70% efficiency over the entire operating range. [Refer to Division 23 Section "Common Motor Requirements for HVAC Equipment".]

        - Provide infinitely adjustable speed control with electric/pneumatic and electronic controls.

        - Internally suspend and isolate fan/motor assembly from casing on rubber isolators.

      - WIRING

        - Factory mount and wire controls.  Mount electrical components in control box with removable cover. Incorporate single point electrical connection to power source.

        - Factory mount transformer for control voltage on electric and electronic control units.  Provide terminal strip in control box for field wiring of thermostat and power source.

        - Factory wire fan to terminal strip.

        - Provide [fused] [unfused] disconnect.

      - CONTROLS

        - Automatic Damper Operator:

          - Operate: Air volume damper [,] [.] [induction damper][,][.] [and automatic volume control.]

          - Electric Actuator: 24 volt [.] [with high limit.] [with remote temperature read and reset capability.]

          - Pneumatic Damper Operator: [8-13] or [3-13] psig ([55-90] or [21-90] kPa) spring range.

          - Maximum Volume Controller and Probe: Pneumatic, with calibration pressure taps for high flow limited proportional variable air volume control.

          - Velocity Reset Controller and Probe: Pneumatic, with calibration pressure taps for pressure independent proportional variable air volume control with means for pressure independent compensating for varying inlet static pressure, with minimum and maximum limits set at reset device, mounted in control box.

        - Thermostat: [Wall-mounted pneumatic] [Diffuser-mounted pneumatic] [Wall-mounted electric] type with appropriate mounting hardware.

        - System Powered Controls:

          - Suitable for operation with duct pressures between 0.25 and 3.0 inches (60 and 750 Pa) static pressure.

          - Factory mounted and piped 5 micron filter, velocity resetting adjustable high limit control and amplifying relay.

          - Aspiring [diffuser] [wall] mounted thermostats.

          - Mount controls in sheet metal enclosure on unit.

          - Provide morning warmup control to sense duct temperature and control unit at maximum airflow during heating mode.

        - Auxiliary Pneumatic Controls:

          - Damper actuators for warm and cold inlet.  Modulate cold damper closed as warm damper opens.  [Provide for dual duct constant volume operation.]

          - Sequence so warm damper actuator may be field adjusted to start opening simultaneous with closing of cold damper or delayed until up to 10 degrees F (6 degrees C) change in room temperature after cold damper has closed.

          - Sequence pneumatic operators with spring ranges selected so warm damper begins to open after cooling damper has fully closed.  Cooling damper to be normally [closed.] [open.] [Provide pneumatic pressure independent controls [or high limit controls] for control of both warm and cold damper, factory calibrated for maximum air flow.]

      - FAN POWERED UNIT CONTROLS

        - [Pneumatic] [Electric] [Electronic] Controls: Contain in NEMA-1 enclosure with access panel sealed from air flow and mounted on side of unit.  Factory mount controls [and thermostat] to accomplish the following specified sequence of operation.

        - Electronic Control, Central System Fan “On” - Occupied Mode:

          - When duct pressure is sensed indicating primary air system operating, thermostat and primary variable volume damper proportions air flow from central system.

          - As thermostat senses reduced cooling demand, volume damper closes.  At field adjustable point, unit fan is energized.  [As cooling demand continues to fall, volume damper closes and fan speed increases.]

          - If central duct system pressure varies, volume damper maintains constant primary air flow.

          - As thermostat senses no cooling, control system closes volume damper.  Before heating is initiated, control enters field adjustable no load band.  On sensing need for heat, heating coil is energized [proportionally.] [in steps.]

        - Electronic Control, Central System Fan “Off” - Unoccupied Mode:

          - Provide field adjustable temperature setback.  On need for heat, terminal unit fan and heating coil are energized.

          - Hold volume damper closed.

        - Pneumatic/Electric Control, Central System Fan “On” - Occupied Mode:

          - As thermostat senses cooling, volume damper proportions air flow from central system.

          - As thermostat senses less cooling and damper closes, [pneumatic/electric] [damper position] switch energizes fan.

          - Electronic fan speed control manually adjusts maximum fan speed to match downstream resistance.

          - Velocity reset primary air control (pressure independent) with maximum and minimum limits.

          - Hi-limit device, factory set, limits maximum primary air flow.

          - As thermostat senses no cooling, control system closes volume damper to stop flow from central system primary air duct before heating is initiated.  On sensing further need for heat, heating coil is energized.

        - Pneumatic/Electric Control, Central System Fan “Off” - Unoccupied Mode:

          - Thermostat cycles fan.

          - Day/night thermostat cycles fan and controls at reduced temperature.

      - TESTS

        - Provide testing of units under provisions of Division 01 Section "General Requirements."

        - Test run [fan/motor combinations,] volume dampers and controls.  Check sequence of operation and air flow limits [corrected for project altitude] at factory prior to shipment.

        - Base performance on tests conducted in accordance with ADC 1062.

        - D.	Automatic flow controller shall be capable of maintaining air flow to within 5 percent of set point with inlet static pressure variations up to [2] [4] inches.

        - Maximum Casing Leakage: 2 percent of design air flow at rated inlet static pressure.

        - Maximum Damper Leakage: 1 percent of design air flow at [one inch] [rated] [     ] inlet static pressure.

- EXECUTION

      - INSTALLATION

        - Install in accordance with manufacturer’s instructions.

        - Provide ceiling access doors or locate units above easily removable ceiling components.

        - Support units individually from structure.  Do not support from adjacent ductwork.

        - Connect to ductwork in accordance with Division 23 Section "Air Coils".

        - Provide minimum of [5 feet] [[5] ft.] of [1 inch] [2 inches] thick lined ductwork downstream of units.

        - Install heating coils in accordance with Division 23 Section "Air Coils".

      - ADJUSTING

        - Reset volume with damper operator attached to assembly allowing flow range modulation from 100 percent of design flow to [0] [50] [     ] percent full flow.  [Set units with heating coils for minimum [50] [     ] percent full flow.]

      - TERMINAL UNIT SCHEDULE

        - Drawing  Code:

          - Location	:

          - Minimum/Maximum

          - Coil Airflow:

          - Static Pressure:

          - Heat Output:

        - Size:

        - Air Flow Range:

          - Minimum:

          - Maximum:

        - Sound Power dB

          - @ 1.0 inch (375 kPa):

          - Inlet Static Pressure:

        - Radiated:

          - 2nd Octave:

          - 3rd Octave:

          - 4th Octave:

          - 5th Octave:

          - 6th Octave:

          - Noise Criterion:

        - Discharge:

          - 2nd Octave:

          - 3rd Octave:

          - 4th Octave:

          - 5th Octave:

          - 6th Octave:

          - Noise Criterion:

        - Coil at Minimum Air

          - Heat Output:

          - Entering Air Temp:

          - Air Temp Rise:

          - Number of Rows:

          - Entering Water Temp:

          - Leaving Water Temp:

          - Electric Input:

          - KW output

END OF SECTION 233600